## Slide 1: BRX Technical Training
Interrupt Service Routines (ISRs)

## Slide 2: ISRs (The Basics)
Choose an ISR if your application requires…
  An interrupting event that needs to be handled immediately (cannot wait on the normal scan of the PLC)
Triggered to run with a configured:
  Event – based on the state of on-board input(s)
  Timer – based on a hardware timer
  Register Match – based on on-board I/O register(s) value(s)
Cannot be invoked in ladders (no instruction exists)
Trigger interrupts normal ladder scan and executes the ISR then returns to normal ladder scan where it left off
The same trigger cannot retrigger itself while running its own ISR
If triggers occur while an ISR is running:
  Those triggers will run after the current ISR according to priority (not according to chronology):
    Event1, Timer1, Match1, Event2, Timer2, Match2, Event3, Timer3, Match3, Event4, Timer4, Match4
No edge-triggered, asynchronous, multi-scan instructions, Stages or calls to Subroutines
Read INs
Ladder Logic
Write OUTs
MyISR

## Slide 3: ISRs
Ladder Logic
Match4 triggers
Match4’s ISR
Event4 triggers
Timer3 triggers
Even though Timer3 occurred after Event4, it is now the highest priority to run
Timer3’s ISR
0
0
0
0
0
0
0
0
0
0
0
0
Match4
Timer4
Event4
Match3
Timer3
Event3
Match2
Timer2
Event2
Match1
Timer1
Event1
Priority
1
1
1
Trigger Register
Having completed running Match4’s ISR, the bit is cleared
Next in line to run is Timer3
Having completed running Timer3’s ISR, the bit is cleared
Next in line to run is Event4
Event4’s ISR
Having completed running Event4’s ISR, the bit is cleared
High
Low

## Slide 4: ISRs (The Basics)
Memory Structure Members
  All readable/writable
  .HasRun (bit) – ON if ISR has run at least one time since last Program-to-Run transition
  .Inhibit (bit)
    Set ON to prevent ISR from being executed when interrupt trigger occurs
    Reset OFF to reenable ISR to run
  .RunCounter (unsigned word) – number of times ISR has run since last Program-to-Run transition
  .Latency (unsigned word) – time in ̲µsec from when the trigger happened to when the ISR is executed
  .ExecutionTime (unsigned word) – time in µsec it takes the ISR to run

## Slide 5: ISRs (Instructions)
Instructions especially designed for ISRs:
  These change the state of the specified bit immediately instead of waiting to change the bit as part of the normal I/O scan between scans
    OUTI – Output Immediate Coil
    RSTI – Reset Immediate Bit
    SETI – Set Immediate Bit
  Immediate instructions take more time because they write to the image register & directly to I/O
    For example:
      OUTI Y0 takes 6-7µs
      OUT Y0 takes 1-2µs
  Termination scan:
    If used in ISR or Subroutine, no termination logic
    If used in Program, Task or Stage, normal termination logic executed
Code Blocks
Read Inputs
Write Outputs
Real Inputs
Real Outputs
Image Register
(OUTs)
Image Register
(INs)
Code Blocks
Read Inputs
Write Outputs
Normal PLC Scan
Normal PLC Scan w/Immediate Instruction
OUTI Encountered
Y0 in Image Register is updated
Y0 in the real world output is written
Code blocks only read/write Image Register