## Slide 1: MQTT (IoT)
Message Queuing Telemetry Transport
(Internet of Things)

## Slide 2: MQTT Fundamentals
MQTT Broker
Publish
Publish
Publish
Publish
Publish
Publish
Subscribe
Subscribe
Subscribe
Subscribe
Publish

## Slide 3: MQTT Terminology (1 of 2)
MQTT Broker
  Receives published topics
  Distributes topics to subscribers
  Keeps Client connections alive
  Sends Last Will & Testament (LWT) to subscribers if a Client “ungracefully disconnects”
MQTT Client
  Can publish topic(s), keep-alive time, Retain bit, QoS, Last Will & Testament
  Can subscribe to topic(s)
Topic
  Name of the data
Payload
  Actual data
Message
  Topic + Payload
QoS (Quality of Service)
  0 = At most once (BRX always, publish & subscribe): transmits message once (relies on TCP)
  1 = At least once : transmits message until it is acknowledged by receiver (may receive more than one)
  2 = Exactly once: transmits message, needs “received” message, asks if it can be “released,” needs “complete” message

## Slide 4: MQTT Terminology (2 of 2)
Publish
  To send a Topic w/Payload to MQTT Broker
Subscribe
  To request a Topic w/Payload update from MQTT Broker
Retain
  Asks MQTT Broker to save the Topic w/Payload even after sending it to all the subscribing Clients
Keep-alive Time
  How often Broker “pings” client to see if he’s there
Last Will & Testament (LWT)
  Topic w/Payload initially sent by an MQTT Client to the MQTT Broker for the Broker to send to other Clients if he is “ungracefully disconnected”

## Slide 5: MQTT Data Exchange
  Publishers are fundamentally separate from Subscribers
    Publishers only care about getting data to Broker
    Broker is fully responsible for getting data to Subscribers
  Clients connect to an MQTT Broker (TCP/IP, MQTT)
  Clients can publish data to topics, e.g.
    host/office/greg/temp, 72.3
  Clients subscribe to topics, e.g.
    host/office/greg/temp
    NOTE: MQTT supports wildcards for topics, but BRX doesn’t
  Clients receive (from Broker) all data published to topics they subscribe to
  Data can be anything (in BRX it can only be strings)
MQTT Broker
Publish
Subscribe
host/office/greg/temp

## Slide 6: MQTT Quality of Service (QoS)
0: At most once
1: At least once
2: Exactly once
BRX Uses QoS = 0 for publish & subscribe
(Lowest Bandwidth)
Basic Peer-to-peer
Financial Transactions

## Slide 7: MQTT Broker – EXAMPLE
MQTT Broker
MQTT Client #1
MQTT Client #2
MQTT Client #3
MQTT Client #4
Topic1 (data), R1
Topic2 (data), R0
LWT:
Topic3 (data), R1
Connect
CLIENT LIST:
#1-KAT:1s
Publish
TOPIC LIST:
Topic1 (data)
Topic2 (data)
LWT:
#1: Topic3 (data)
SUBSCRIBE:
No Subscribers
Connect
#3-KAT:5s
Topic1
Topic3
Subscribe
#3: T1, T3
Topic1 exists & is retained
(data)
Broker sends Topic1 to #3
Topic3 not sent because it is LWT & #1 is still alive
Connect
Topic1
Topic2
Topic6
Subscribe
#4: T1, T2, T6
(data)
Broker sends Topic1 to #4
Topic2 & Topic6 do not exist
#4-KAT:30s
Topic2 data changes so Client publishes change
Client#4 needs Topic2
(data)
Broker sends Topic2 to #4
Topic2 not retained
Topic2 not retained
Connect
#2-KAT:30s
Topic4 (data), R0
Topic5 (data), R0
Topic6 (data), R0
Publish
Topic4 (data)
Topic5 (data)
Topic6 (data)
(data)
(data)
Client#4 needs Topic6
Broker sends Topic6 to #4
Topic4, 5 & 6 not retained
Client #1 is abruptly cut off!
LWT sent to Client #3
Topic3 is retained
Topic3 is retained
If Client #1 had disconnected in a normal way: 1. Broker deletes LWT (Topic3)
2. Broker does not send Topic3 to anyone
(data)
(data)

## Slide 8: MQTT in BRX (Configuration)
Must create MQTT Client Device
Device Name
  Referenced by the MQTTPUB & MQTTSUB instructions
MQTT Server Address
  Use Server Name
    URL of Broker; will be resolved when instructions are executed
  Use IP Address
    IP address of Broker
Other Settings
  Server Port
    1883 (MQTT default)
  Comm Timeout
    How long Device will wait for response from Broker before an error
  Session Keep Alive
    Client tells Broker this time upon connection
    If Client doesn’t talk to Broker in this time period, Broker will ping him to make sure he’s still there.

## Slide 9: MQTT in BRX (Configuration)
Enable Account Authentication
  Some MQTT Brokers require authentication with Username & Password
Enable Will
  If Client is “ungracefully disconnected” from Broker, Broker will send this Topic to any Client that has subscribed to it
  Topic:
    Text name of Topic of Last Will & Testament
  Payload:
    Text of the data of the Last Will & Testament
  Retain Topic
    If this is checked, and this Client is “ungracefully disconnected,” Broker will hold this value and send it to any other Client who subscribes to the Topic in the future

## Slide 10: MQTTPUB “IoT Publish MQTT Topics”
MQTTPUB “IoT Publish MQTT Topics”
MQTT Client Device
  MQTT Device name you just created
  Enable
    Once on Leading Edge
      Makes TCP connection to Broker
      Publishes listed Topics
      Disconnects from Broker
    Continuous on Power Flow at Interval
      Constant or Variable
        Every interval, instruction scans list & does what each Topic’s Publish rule states

## Slide 11: MQTTPUB “IoT Publish MQTT Topics”
Optional Topic Prefix
  Prepended text for all Topics in list
Topic List
  Up to 50 Topics to publish
  When instruction is executed each Topic in list is published according to Publish Interval Setting rule
  Topic
    Use common Optional Topic Prefix – check to use the prepended text
    Enter a name for a Topic that makes sense to you
  Payload - Enter the string element or a literal string in quotes
  Retain – tells the MQTT server you want this Topic to be retained
    NOTE: to delete a retained Topic from the MQTT server, send another Retained Topic with an empty Payload (e.g. “”, or an empty string Element)
  Publish Interval Setting
    Publish at Interval only if value changed since the last Interval
    Publish at every Interval even if the value has not changed

## Slide 12: MQTTPUB “IoT Publish MQTT Topics”
On Success and On Error
  Set a bit, or JMP to Stage
Extended Error Information
  Must be a double-word
    Upper word contains entry number of the first Topic that failed (e.g. D0:W1)
    Lower word contains error code (e.g. D0:W0)
Ladder Stage editing helper
  Automatically create the SG box for any NEW stage number – if either of the On Success or On Error selection is “JMP to Stage” this option can be checked
    Below this rung
    At end of code-block
VALUE | ERROR | DESCRIPTION
0 | <none> | <none>
57 | Unexpected MQTT Response | MQTT Broker response not properly formed
58 | MQTT Broker rejected | MQTT Broker refused Topic (Username? Password? Security violation?)
59 | Out of resources (MQTTSUB only) | > 10 MQTTSUBs or > 100 Topics using same MQTT Client device
60 | Invalid Topic | Topic is empty
61 | Duplicate Topic | Topic already subscribed to in different MQTTSUB

## Slide 13: MQTTSUB “IoT Subscribe MQTT Topics”
MQTTSUB “IoT Subscribe MQTT Topics”
MQTT Client Device
  MQTT Device name you just created
  Enable to subscribe to Topics in the Topic list, and keep enabled for them to constantly update

## Slide 14: MQTTSUB “IoT Subscribe MQTT Topics”
Optional Topic Prefix
  Prepended text for all Topics in list
Topic List
  Up to 50 Topics to subscribe to
  Topic
    Use common Optional Topic Prefix – check to use the prepended text
    Enter a name for a Topic you want to subscribe to
  Payload - enter the string Element where the Topic’s data will be stored

## Slide 15: MQTTSUB “IoT Subscribe MQTT Topics”
Instruction Operation
  When 1st enabled:
    On Success & On Error bits are turned OFF
      NOTE: Instruction must remain enabled for all subscribed Topics to keep updating.
    Attempts to subscribe to all Topics
      If > 0 successfully subscribed then On Success bit comes ON
      If all subscriptions failed then On Error bit comes ON
  While kept enabled:
    Continuously updates all Topics it receives from MQTT Broker
      NOTE: It does NOT try to re-subscribe to Topics that may have failed initially
  When disabled:
    Attempts to unsubscribe from all Topics
      If > 0 successfully unsubscribed then On Success bit comes ON
      If all Topics failed to unsubscribe then On Error bit comes ON
    If no other MQTTSUB or MQTTPUB instructions are using the MQTT Client Device, then it will cause the MQTT Client to disconnect from the MQTT Broker (TCP disconnect)
Extended Error Information is same as MQTTPUB