## Slide 1: Do-more Technical Training
Onboard Clock

## Slide 2: Onboard Clock
Accuracy: 1.53 minutes/month
Stored as UTC (Coordinated Universal Time)
  Stored in $UTC (DST21)
  Uses 1970 Epoch: number of seconds since 00:00:00, 01-January-1970
Adjusted by time zone
  $TimeZone (DST384) – number of minutes
Adjusted by Daylight Savings Time
  $SummerTime (ST768) – ON +1 hour
Adjusted time stored
  $LocalTime (DST22) – UTC adjusted seconds
NOTE: These values are not very useful
Seconds
1970 Epoch

## Slide 3: Onboard Clock
$LocalTime (DST22) is also stored as Date/Time structure:
  $Now (SDT0) structure members:
    Year – unsigned word
    Month – unsigned byte
    Day – unsigned byte
    DayOfWeek – unsigned byte
      0 = Sunday, 1 = Monday, etc.
    Hour – unsigned byte
    Minute – unsigned byte
    Second – unsigned byte
    Date – signed Dword
      YYYYMMDD (use “Date Field” to see)
    Time – signed Dword
      DDHHMMSS (use “Time Field” so see)
  NOTE: Date & Time structure members are not very useful except for some HMI displays
  $SysShutdown (SDT1) – date/time of last power OFF
  $SysStartup (SDT2) – date/time of last power ON

## Slide 4: Onboard Clock (The Basics)
$UTC (DST21)
$TimeZone (DST284)
$SummerTime (ST768)
$LocalTime (DST22)
$Now (SDT0)
1,427,208,203 seconds
-300 minutes
ON = +1 hour
1,427,193,803
seconds
$Now.Year (2015) $Now.Month (3)
$Now.Day (24)
$Now.DayOfWeek (2)
$Now.Hour (10)
$Now.Minute (43)
$Now.Second (23)
-18,000 seconds
= 1,427,190,203
+3600 seconds
= 1,427,193,803
1970 Epoch
Minutes
Bit
1970 Epoch
Date/Time Structure

## Slide 5: Onboard Clock
Setting the system clock:
  Manually:
    Set PLC Clock dialog
  Auomatically:
    (1) TimeSync function
    (2) NETTIME “SNTP Client” instruction
    (3) SETTIME “Set PLC Date/Time” instruction

## Slide 6: Onboard Clock
Manual Setting:
  PLC  Set PLC Clock…

## Slide 7: Onboard Clock
Automatic Setting:
  (1) TimeSync function: CPU Configuration  TimeSync Configuration
      Client:
        Listens for server’s time-sync packet
        If heard 
          $TimeSynced (ST23) = ON
          Sets onboard clock  $UTC (DST21)
          Keeps listening (times down from Update Interval)
        If Update Interval times out 
          $TimeSynced (ST23) = OFF
          Keeps listening (times down from Update Interval)
      Server: transmits 3 time-sync packets (5 second intervals) every Update Interval)
      Alternate:
        Normally a Client
        If Update Interval times out + 15 seconds 
          Becomes the new Server
      Update Interval: 0 – 32,767 minutes (22 days)

## Slide 8: Onboard Clock
Automatic Setting:
  (2) NETTIME “SNTP Client” instruction
    Retrieves date/time from an SNTP (Simple Network Time Protocol) Server & stored in $UTC (DST21)
    Parameters:
      Device – onboard Ethernet port
      SNTP Server IP Address
        Fixed IP Address – IP address of SNTP Server
        Variable IP Address – (32-bit word) variable IP address of SNTP Server commonly obtained by DNSLOOKUP “Name to IP Address” instruction
      UDP Port Number – SNTP Protocol default is 123
      Network Timeout – 1 to 65.535 seconds
      On Success, On Error – Action to take
    Instruction is leading-edge triggered
    NOTE: NTP protocol is not supported
Notes: * Program NETTIME using Richard’s SNTP server IP address

## Slide 9: Onboard Clock
Automatic Setting:
  (3) SETTIME “Set PLC Date/Time” instruction
    Writes date/time to system clock
      Writes $UTC (DST21) directly, or…
      Writes $LocalTime (DST22) then…
      …back-adjusts $UTC (DST21) based on:
        $TimeZone (DST284) value
        $SummerTime (ST768) bit
    Parameters:
      Source Date/Time – structure containing setting
      Source Type:
        Local Time – Source Date/Time represents local time
        UTC Time – Source Date/Time represents UTC time
    Instruction is leading-edge triggered
$UTC (DST21)
$TimeZone (DST284)
$SummerTime (ST768)
$LocalTime (DST22)
$Now (SDT0)

## Slide 10: Onboard Clock
Programmatic use:
  Assignment:
    MEMCOPY “Copy Memory Range”
    MOVE “Move Value”
  Conversion:
    DT2EPOCH “Convert Date/Time to 1970 Epoch”
    EPOCH2DT “Convert Epoch to Date/Time”
    MATH  NOW() function – Get Date/Time as a 32-bit integer (1970 Epoch)
  Math-style operations:
    DTCMP “Compare Date/Time”
    DTDIFF “Difference between two Date/Times”
    DTOFFSET “Add Offset to Date/Time”

## Slide 11: Onboard Clock
Programmatic use:
  Assignment:
    MEMCOPY “Copy Memory Range”
      Use it to copy complete Date/Time structures

## Slide 12: Onboard Clock
Programmatic use:
  Assignment:
    MOVE “Move Value”
      Use it to copy single Date/Time structure members

## Slide 13: Onboard Clock
Programmatic use:
  Conversion:
    DT2EPOCH “Convert Date/Time to 1970 Epoch”
      Converts a Date/Time structure to 1970 Epoch value
      Parameters:
        Date/Time – structure to convert
        1970 Epoch – location of converted value

## Slide 14: Onboard Clock
Programmatic use:
  Conversion:
    EPOCH2DT “Convert Epoch to Date/Time”
      Converts a 1970 Epoch value to Date/Time structure
      Parameters:
        1970 Epoch – seconds to convert
        Date/Time – structure of converted value

## Slide 15: Onboard Clock
Programmatic use:
  Conversion:
    MATH “Calculate Express” NOW() function
      Converts the Date/Time structure $Now (SDT0) to 1970 Epoch value

## Slide 16: Onboard Clock
Programmatic use:
  Math-style operations:
    DTCMP “Compare Date/Time”
      Compares two Date/Time structures
      Parameters:
        First Date/Time – 1st structure to be compared
        Second Date/Time – 2nd structure to be compared
        Compare:
          Compare Date and Time
          Compare Date Only
          Compare Time Only
        Set if First Equals Second
        Set if First is Before Second
        Set if First is After Second

## Slide 17: Onboard Clock
Programmatic use:
  Math-style operations:
    DTDIFF “Difference Between Two Date/Times”
      Calculates the number of seconds of time between two Date/Time structures
      Parameters:
        Date/Time A
        Date/Time B
        Difference DTA-DTB in seconds

## Slide 18: Onboard Clock
Programmatic use:
  Math-style operations:
    DTOFFSET “Add Offset to Date/Time”
      Adds time to a Date/Time structure
      Parameters:
        Starting Date/Time
        Offset
          Constant – will be normalized
            Negative
          Variable – in seconds
        Ending Date/Time