## Slide 1: Do-more Technical Training
System Configuration
(CPU Configuration)

## Slide 2: System Configuration
CPU Configuration
  Serial Port Mode
  Modbus/TCP Server Configuration
  TimeSync Configuration
  Default Watchdog Timeout
  Ethernet I/O Master
  Internal Ethernet Port
  EtherNet/IP Explicit Message Server
Notes: Launchpad: nothing new here
Project Browser:
  Buttons
    Control Logic Filter – Display filter
    New Code Block – Create new code blocks
    Execution Order – Change execution order of blocks
    Status – Shows which blocks are enabled to run
    Sort Code Blocks – Change display order
    Sort Memory – Change display order
  Control Logic
  Configuration
  Tools
Debug View
  NOTE: Message Dump – enables dump to Do-more Logger, $EnableMsgDump (ST36)
Data View
PID Overview

## Slide 3: System Configuration
CPU Configuration
  Serial Port Mode
    RS-232, RJ12 connector
    Non-isolated, full duplex, ESD & surge protection
    Power pins 1-2, reverse polarity & overload protection
    RXD, TXD load = 3KΩ 1000pF
    D2=DSCBL, USB-RS3232 w/D2-DSCBL, FA-CABKIT, FA-ISOCON (RS-232 to RS-422/485), EA-MG-PGM
Notes: Launchpad: nothing new here
Project Browser:
  Buttons
    Control Logic Filter – Display filter
    New Code Block – Create new code blocks
    Execution Order – Change execution order of blocks
    Status – Shows which blocks are enabled to run
    Sort Code Blocks – Change display order
    Sort Memory – Change display order
  Control Logic
  Configuration
  Tools
Debug View
  NOTE: Message Dump – enables dump to Do-more Logger, $EnableMsgDump (ST36)
Data View
PID Overview

## Slide 4: System Configuration
CPU Configuration
  Serial Port Mode
    Do-more Programming (default)
    K Sequence Server
      Serves up DL-memory
    Modbus RTU Server (Slave)
      Serves up M-memory
    Modbus RTU Client (Master)
      Uses the MRX / MWX instructions
    General Purpose – (Master/Slave)
      Uses the STREAMIN / STREAMOUT instructions
Notes: Launchpad: nothing new here
Project Browser:
  Buttons
    Control Logic Filter – Display filter
    New Code Block – Create new code blocks
    Execution Order – Change execution order of blocks
    Status – Shows which blocks are enabled to run
    Sort Code Blocks – Change display order
    Sort Memory – Change display order
  Control Logic
  Configuration
  Tools
Debug View
  NOTE: Message Dump – enables dump to Do-more Logger, $EnableMsgDump (ST36)
Data View
PID Overview

## Slide 5: System Configuration
CPU Configuration
  Serial Port Mode
    Do-more Programming (default)
      Baud Rate: 300, 1200, 2400, 4800, 9600, 19.2K, 38.4K, 57.6K, 115.2K
      Data Bits: 7, 8
      Stop Bits: 1, 2
      Parity: None, Odd, Even
      Transmit Control:
        Unconditional – Xmit w/o delay
        Wait for CTS
        Delayed 5ms, 50ms, 250ms, 500ms – Xmit after asserting RTS + delay
      RTS Control:
        Follows Transmitter – RTS controlled by xmitter
        Manual – RTS controlled by IntSerial.RTS
        Off/On – Forces RTS
Notes: Launchpad: nothing new here
Project Browser:
  Buttons
    Control Logic Filter – Display filter
    New Code Block – Create new code blocks
    Execution Order – Change execution order of blocks
    Status – Shows which blocks are enabled to run
    Sort Code Blocks – Change display order
    Sort Memory – Change display order
  Control Logic
  Configuration
  Tools
Debug View
  NOTE: Message Dump – enables dump to Do-more Logger, $EnableMsgDump (ST36)
Data View
PID Overview

## Slide 6: System Configuration
CPU Configuration
  Serial Port Mode
    K Sequence Server
      Serves up DLX, DLY, DLC & DLV
      Station: 1 - 90
      Baud Rate: 300, 1200, 2400, 4800, 9600, 19.2K, 38.4K, 57.6K, 115.2K
      Data Bits: 7, 8
      Stop Bits: 1, 2
      Parity: None, Odd, Even
      Transmit Control:
        Unconditional – Xmit w/o delay
        Wait for CTS
        Delayed 5ms, 50ms, 250ms, 500ms – Xmit after asserting RTS + delay
      RTS Control:
        Follows Transmitter – RTS controlled by xmitter
        Manual – RTS controlled by IntSerial.RTS
        Off/On – Forces RTS
Notes: Launchpad: nothing new here
Project Browser:
  Buttons
    Control Logic Filter – Display filter
    New Code Block – Create new code blocks
    Execution Order – Change execution order of blocks
    Status – Shows which blocks are enabled to run
    Sort Code Blocks – Change display order
    Sort Memory – Change display order
  Control Logic
  Configuration
  Tools
Debug View
  NOTE: Message Dump – enables dump to Do-more Logger, $EnableMsgDump (ST36)
Data View
PID Overview

## Slide 7: System Configuration
CPU Configuration
  Serial Port Mode
    Modbus RTU Server (Slave)
      Serves up MI, MC, MIR, & MHR
      Unit ID: 0 - 255
      Baud Rate: 300, 1200, 2400, 4800, 9600, 19.2K, 38.4K, 57.6K, 115.2K
      Data Bits: 7, 8
      Stop Bits: 1, 2
      Parity: None, Odd, Even
      Transmit Control:
        Unconditional – Xmit w/o delay
        Wait for CTS
        Delayed 5ms, 50ms, 250ms, 500ms – Xmit after asserting RTS + delay
      RTS Control:
        Follows Transmitter – RTS controlled by xmitter
        Manual – RTS controlled by IntSerial.RTS
        Off/On – Forces RTS
Notes: Launchpad: nothing new here
Project Browser:
  Buttons
    Control Logic Filter – Display filter
    New Code Block – Create new code blocks
    Execution Order – Change execution order of blocks
    Status – Shows which blocks are enabled to run
    Sort Code Blocks – Change display order
    Sort Memory – Change display order
  Control Logic
  Configuration
  Tools
Debug View
  NOTE: Message Dump – enables dump to Do-more Logger, $EnableMsgDump (ST36)
Data View
PID Overview

## Slide 8: System Configuration
CPU Configuration
  Serial Port Mode
    Modbus RTU Client (Master)
      Master has no Unit ID address
      Use MRX & MWX instructions
      Timeout: 0 – 32,767 ms; time for slave to respond
      Retries: 0 – 255
      Inter-packet Delay: 0 – 65,535 µs; between packets
      Baud Rate: 300, 1200, 2400, 4800, 9600, 19.2K, 38.4K, 57.6K, 115.2K
      Data Bits: 7, 8
      Stop Bits: 1, 2
      Parity: None, Odd, Even
      Transmit Control:
        Unconditional – Xmit w/o delay
        Wait for CTS
        Delayed 5ms, 50ms, 250ms, 500ms – Xmit after asserting RTS + delay
      RTS Control:
        Follows Transmitter – RTS controlled by xmitter
        Manual – RTS controlled by IntSerial.RTS
        Off/On – Forces RTS
Notes: Launchpad: nothing new here
Project Browser:
  Buttons
    Control Logic Filter – Display filter
    New Code Block – Create new code blocks
    Execution Order – Change execution order of blocks
    Status – Shows which blocks are enabled to run
    Sort Code Blocks – Change display order
    Sort Memory – Change display order
  Control Logic
  Configuration
  Tools
Debug View
  NOTE: Message Dump – enables dump to Do-more Logger, $EnableMsgDump (ST36)
Data View
PID Overview

## Slide 9: System Configuration
CPU Configuration
  Serial Port Mode
    General Purpose
      Use STREAMIN & STREAMOUT instructions
      Baud Rate: 300, 1200, 2400, 4800, 9600, 19.2K, 38.4K, 57.6K, 115.2K
      Data Bits: 7, 8
      Stop Bits: 1, 2
      Parity: None, Odd, Even
      Transmit Control:
        Unconditional – Xmit w/o delay
        Wait for CTS
        Delayed 5ms, 50ms, 250ms, 500ms – Xmit after asserting RTS + delay
      RTS Control:
        Follows Transmitter – RTS controlled by xmitter
        Manual – RTS controlled by IntSerial.RTS
        Off/On – Forces RTS
Notes: Launchpad: nothing new here
Project Browser:
  Buttons
    Control Logic Filter – Display filter
    New Code Block – Create new code blocks
    Execution Order – Change execution order of blocks
    Status – Shows which blocks are enabled to run
    Sort Code Blocks – Change display order
    Sort Memory – Change display order
  Control Logic
  Configuration
  Tools
Debug View
  NOTE: Message Dump – enables dump to Do-more Logger, $EnableMsgDump (ST36)
Data View
PID Overview

## Slide 10: Built-In Ethernet Port
10Base-T / 100Base-T RJ45 connector
Isolated, full duplex, ESD & surge protection
10 / 100 Mbps
Patch (straight-thru) or crossover cabling
PROTOCOL | NOTES: | PROTOCOL | NOTES:
Do-more programming | Always enabled – serves up all Do-more memory | SMTP | EMAIL
Peerlink | PEERLINK | SNTP | NETTIME
Modbus TCP | Client (master) – MRX / MWX Server (slave) – serves up MI, MC, MIR, MHR | Custom UDP | PACKETIN, PACKETOUT
DirectLOGIC RX/WX | Always enabled – serves up DLX, DLY, DLC, DLV | Custom TCP | Client (master) – OPENTCP, STREAMIN, STREAMOUT Server (slave) – TCPLISTEN, STREAMIN, STREAMOUT
K-sequence | Server (slave) – serves up DLX, DLY, DLC, DLV | Ethernet I/O | Maps 16 EBC100 slaves I/O
EtherNet/IP | Client (master) - EIPMSG Server (slave) – serves up configured blocks | ICMP | PING
DNS | DNSLOOKUP | TimeSync | Client (master) Server (slave)
System Configuration
Notes: Launchpad: nothing new here
Project Browser:
  Buttons
    Control Logic Filter – Display filter
    New Code Block – Create new code blocks
    Execution Order – Change execution order of blocks
    Status – Shows which blocks are enabled to run
    Sort Code Blocks – Change display order
    Sort Memory – Change display order
  Control Logic
  Configuration
  Tools
Debug View
  NOTE: Message Dump – enables dump to Do-more Logger, $EnableMsgDump (ST36)
Data View
PID Overview

## Slide 11: System Configuration
CPU Configuration
  Modbus/TCP Server Configuration
    Serves up MI (Inputs), MC (Coils), MIR (Input Registers), MHR (Holding Registers)
    Enable Modbus/TCP Server: enabled by default
    Maximum Concurrent Sessions: 1 – 16
    Client Inactivity Timeout: closes TCP connection if master is not heard from; 0 – 65,535 seconds
    TCP Port Number: 0 – 65,535
Notes: Launchpad: nothing new here
Project Browser:
  Buttons
    Control Logic Filter – Display filter
    New Code Block – Create new code blocks
    Execution Order – Change execution order of blocks
    Status – Shows which blocks are enabled to run
    Sort Code Blocks – Change display order
    Sort Memory – Change display order
  Control Logic
  Configuration
  Tools
Debug View
  NOTE: Message Dump – enables dump to Do-more Logger, $EnableMsgDump (ST36)
Data View
PID Overview

## Slide 12: System Configuration
CPU Configuration
  TimeSync Configuration
    Automatic time sync network
      1 server
      1 or more alternate server(s)
      1 or more client(s)
    TCP/IP broadcast (network domain)
    Disabled: default
    Client:
      Listens for server’s time-sync packet
      If heard 
        $TimeSynced (ST23) = ON
        Sets real-time clock
        Keeps listening (times down from Update Interval)
      If Update Interval times out 
        $TimeSynced (ST23) = OFF
        Keeps listening (times down from Update Interval)
    Server: transmits 3 time-sync packets (5 second intervals) every Update Interval)
    Alternate:
      Normally a Client
      If Update Interval times out + 15 seconds 
        Becomes the new Server
    Update Interval: 0 – 32,767 minutes (22 days)
Notes: Launchpad: nothing new here
Project Browser:
  Buttons
    Control Logic Filter – Display filter
    New Code Block – Create new code blocks
    Execution Order – Change execution order of blocks
    Status – Shows which blocks are enabled to run
    Sort Code Blocks – Change display order
    Sort Memory – Change display order
  Control Logic
  Configuration
  Tools
Debug View
  NOTE: Message Dump – enables dump to Do-more Logger, $EnableMsgDump (ST36)
Data View
PID Overview

## Slide 13: System Configuration
CPU Configuration
  Default Watchdog Timeout
    Time allowed for 1 scan
    Default Timeout: 50 – 65,535 ms
    $WatchdogTimeVal (DST23)
    If exceeded 
      STOP mode
      Error message in System Information
      ERR light
Notes: Launchpad: nothing new here
Project Browser:
  Buttons
    Control Logic Filter – Display filter
    New Code Block – Create new code blocks
    Execution Order – Change execution order of blocks
    Status – Shows which blocks are enabled to run
    Sort Code Blocks – Change display order
    Sort Memory – Change display order
  Control Logic
  Configuration
  Tools
Debug View
  NOTE: Message Dump – enables dump to Do-more Logger, $EnableMsgDump (ST36)
Data View
PID Overview

## Slide 14: System Configuration
CPU Configuration
  Ethernet I/O Master
    Enable Ethernet I/O Master
      Creates $EthIOMaster structure
      Creates Ethernet I/O Master entry in the I/O Configuration
Ethernet I/O Master Structure Members (68) |  | 
Warning | SlaveErrors | SlavexError
Error | SlavexRetryCnt | SlavexErrorInfo
SlaveWarnings | SlavexUpdateCnt | x = 0-15
Notes: Launchpad: nothing new here
Project Browser:
  Buttons
    Control Logic Filter – Display filter
    New Code Block – Create new code blocks
    Execution Order – Change execution order of blocks
    Status – Shows which blocks are enabled to run
    Sort Code Blocks – Change display order
    Sort Memory – Change display order
  Control Logic
  Configuration
  Tools
Debug View
  NOTE: Message Dump – enables dump to Do-more Logger, $EnableMsgDump (ST36)
Data View
PID Overview

## Slide 15: System Configuration
CPU Configuration
  Internal Ethernet Port
    Configure IP parameters
    Normal Do-more Designer Programming session uses TCP/IP Port # 28,784 (7070 hex).
    Checking Enable Secondary Ethernet Connection allows an additional TCP/IP Port # of your choice.
    UDP Port Number: 5000 – 65,535 (except 28,784)
Notes: Launchpad: nothing new here
Project Browser:
  Buttons
    Control Logic Filter – Display filter
    New Code Block – Create new code blocks
    Execution Order – Change execution order of blocks
    Status – Shows which blocks are enabled to run
    Sort Code Blocks – Change display order
    Sort Memory – Change display order
  Control Logic
  Configuration
  Tools
Debug View
  NOTE: Message Dump – enables dump to Do-more Logger, $EnableMsgDump (ST36)
Data View
PID Overview

## Slide 16: System Configuration
CPU Configuration
  EtherNet/IP Explicit Message Server
    EtherNet/IP Settings…
Notes: Launchpad: nothing new here
Project Browser:
  Buttons
    Control Logic Filter – Display filter
    New Code Block – Create new code blocks
    Execution Order – Change execution order of blocks
    Status – Shows which blocks are enabled to run
    Sort Code Blocks – Change display order
    Sort Memory – Change display order
  Control Logic
  Configuration
  Tools
Debug View
  NOTE: Message Dump – enables dump to Do-more Logger, $EnableMsgDump (ST36)
Data View
PID Overview